BEFORE THE PUBLIC UTILITIES COMMISSION

STATE OF COLORADO

Docket No.  09A-324E

1

IN THE MATTER OF THE APPLICATION OF TRI-STATE GENERATION AND TRANSMISSION ASSOCIATION, INC., (A) FOR A CERTIFICATE OF PUBLIC CONVENIENCE AND NECESSITY FOR THE SAN LUIS VALLEY-CALUMET-COMANCHE TRANSMISSION PROJECT, (B) FOR SPECIFIC FINDINGS WITH RESPECT TO EMF AND NOISE, AND (C) FOR APPROVAL OF OWNERSHIP INTEREST TRANSFER AS NEEDED WHEN PROJECT IS COMPLETED

Docket No.  09A-325E

2

IN THE MATTER OF THE APPLICATION OF PUBLIC SERVICE COMPANY OF COLORADO  (A) FOR A CERTIFICATE OF PUBLIC CONVENIENCE AND NECESSITY FOR THE SAN LUIS VALLEY-CALUMET-COMANCHE TRANSMISSION PROJECT, (B) FOR SPECIFIC FINDINGS WITH RESPECT TO EMF AND NOISE, AND (C) FOR APPROVAL OF OWNERSHIP INTEREST TRANSFER AS NEEDED WHEN PROJECT IS COMPLETED

CROSS ANSWER TESTIMONY OF INEZ G. DOMINGUEZ

###### STAFF OF THE COLORADO PUBLIC UTILITIES COMMISSION

December 2, 2009

TABLE OF CONTENTS

SECTION                                                                                                                             PAGE

I.	INTRODUCTION                                                                                                       1

II.	PURPOSE OF CROSS-ANSWER TESTIMONY                                                   1

III.	COMMENTS REGARDING MR. DAUPHINAIS’ PROPOSAL                          2

TO ADD 250-525 MW OF NEW GENERATION IN THE SAN

LUIS VALLEY WITHOUT ANY NEW TRANSMISSION LINE

ADDITIONS

IV.	COMMENTS REGARDING THE ADDITION OF ANOTHER                           10

PONCHA-SAN LUIS 230KV LINE AND THE 475-575 MW

OF NEW GENERATION THIS NEW LINE CAN SUPPORT

IN THE SAN LUIS VALLEY

V.	COMMENTS REGARDING HOW MR. DAUPHINAIS’ PROPOSAL	   11	     IS A SHORT TERM SOLUTION TO THE POTENTIAL OF SOLAR GENERATION IN THE SAN LUIS VALLEY

- CONCLUSIONS 							                           15

VII.       SUMMARY AND RECOMMENDATIONS                                                          18

APPENDIX A

EXHIBITS

Exhibit IGD-10, 1 page

Exhibit IGD-11, 1 page

Exhibit IGD-12, 47 pages

I.     INTRODUCTION

Q.	PLEASE STATE YOUR NAME AND BUSINESS ADDRESS.

A.	My name is Inez G. Dominguez.  My business address is 1560 Broadway, Suite 250, Denver, Colorado 80202.

Q.	BY WHOM ARE YOU EMPLOYED AND IN WHAT CAPACITY?

A.	I am employed by the Colorado Public Utilities Commission (Commission) as a Staff Engineer.

Q.	DID YOU PREVIOUSLY FILE TESTIMONY IN THIS PROCEEDING?

A.	Yes, I filed Answer Testimony on behalf of Staff on October 28, 2009.

II.     PURPOSE OF CROSS-ANSWER TESTIMONY

Q.	WHAT IS THE PURPOSE OF YOUR CROSS-ANSWER TESTIMONY IN THIS 	PROCEEDING?

A.	The purpose of this testimony is to provide Staff’s analysis of Mr. James R. Dauphinais’ Answer Testimony submitted on behalf of Blanca Ranch Holdings, LLC and Trinchera Ranch Holdings, LLC in the instant docket relating to the application of Public Service Company of Colorado and Tri-State Generation and Transmission Association, Inc. (the Utilities) for a certificate of public convenience and necessity (CPCN) for the San Luis-Calumet-Comanche Transmission Project.  My Cross-Answer Testimony comments Mr. Dauphinais’ proposal:

1.	to add 250-525 MW of new generation in the San Luis Valley area without any new transmission line additions;

2.	to add another Poncha-San Luis 230kV line and the 475-575 MW of new generation this new line can support in the San Luis Valley; and

3.	for generation that is a short term solution for the potential solar generation in the San Luis Valley.

- COMMENTS REGARDING THE 250-525 MW OF NEW

GENERATION IN THE SAN LUIS VALLEY WITHOUT

ANY NEW TRANSMISSION LINE ADDITIONS

Q.	DO YOU HAVE COMMENTS REGARDING MR. DAUPHINAIS’  STUDY ON 	THE 	POSSIBILITY OF ADDING 250-525 MW OF NEW GENERATION IN 	THE 	SAN LUIS VALLEY WITHOUT ADDITIONAL TRANSMISSION LINES?

A.	Yes.  Before I directly respond to Mr. Dauphinais’ comments, let me lay a foundation for 	my response.  Mr. Dauphinais’ study results are summarized on Page iii of his 	testimony entitled “Summary of Answer Testimony of James R. Dauphinais.”

Q.	WHAT ARE YOUR PRELIMINARY REMARKS?

A.	The San Luis Valley area electric system is a radial system, meaning the local peak load of 139 MW (125 MW of load plus 14 MW of losses) in the study is much greater than the amount of local generation of about 42 MW (34 MW of combustion turbines (CT) generation and 8 MW of solar generation).  The remaining 97 MW are then supplied by the Poncha-Sargent-San Luis 115kV line and the Poncha-San Luis 230kV line.  A 69kV line from Poncha also feeds a small portion of the load.  A 2008 Load Duration Curve for the San Luis Valley area shows about a 133 MW peak in July and a minimum load of about 43 MW in November (reference Exhibit IGD -10).  The load during this off-peak condition is 32% of the peak.  From the table labeled “Monthly Min” on Exhibit IGD-10, eight months out of the year show the minimum load to be less than 50 MW with the spring months of March, April, and May having an average minimum load of 46 MW and the fall months of September, October, and November having an average minimum load of about 44 MW.  These spring and fall averages are within three MW of the minimum peak.  So the off-peak load in the San Luis Valley can be significantly lower than the maximum summer peak load.  Because of the radial nature of the San Luis Valley electric system and the linear nature of the power flow (MW) into it, my analysis of matching generation to load will be done using simple arithmetic.  The arithmetic numbers will then raise flags where these numbers can then be fine tuned if need be with power flow and stability simulations.

An ideal situation for the San Luis Valley would be for the local generation level to be the same as the local load with the transmission lines into the San Luis Valley serving as a regulation source for the frequency and minor load/generation changes.  As suggested by Mr. Dauphinais, it is possible that at the time of the 139 MW peak, 150 MW of generation there would resolve the load serving reliability issues with the loss of the Poncha-San Luis 230kV line.  However, to totally resolve the reliability issue, the generation has to be online during the time when the valley load is 65 MW and higher.  It is possible that solar generation may not be on at night when the sun is not shining and the load may be 65 MW and higher, putting the San Luis Valley area at risk for the Poncha-San Luis Valley 230kV outage.

Following Mr. Dauphinais’ approach, my educated guess for the amount of additional generation the San Luis Valley can accommodate would be 65 MW plus the minimum load of the year, roughly another 44 MW (32%*139 MW) for a total of 109 MW, which would also include the 34 MW of CT plus the 8 MW of existing solar generation, leaving a balance of new generation of 67 MW.  This total of 109 MW of generation would allow load service in the valley plus a 65 MW export out of the valley during minimum load conditions.

Q.	WHAT ABOUT THE 250 MW GENERATION SCENARIO?

A.	For the 250 MW new generation scenario during the peak, we can assume the 34 MW of CT would be off line leaving 258 MW of solar generation on line in the San Luis Valley.  With a 139 MW load, the remaining 119 MW of excess generation would need to flow out of the valley on the 115kV and 230kV lines to the Poncha Substation.  Electrically, this system would work under system intact conditions.  With an outage of the San Luis-Poncha 230kV line, the San Luis-Sargent 115kV line would have to carry about 119 MW and the Sargent-Poncha 115kV line would have to carry about 94 MW after dropping off 25 MW of load at the Sargent Substation.  For the peak condition, the arithmetic shows that this may work from a power flow standpoint.  However, this case would have to be tested for stability since the Poncha Substation 115kV bus is not a very strong bus.  This observation is made from the fact that 65 MW flowing on the Poncha-Sargent 115kV line into the San Luis Valley is the trigger point for voltage problems in the San Luis Valley with a Poncha-San Luis 230kV outage.  Similarly with a Poncha-San Luis 230kV outage and 65 MW flowing out of the San Luis Valley on the Sargent-Poncha 115kV line, 65 MW is also a flag for potential voltage problems on the 115kV system connected to the Poncha 115kV bus.  Also, note that during daylight hours when generation may be at peak and the load is significantly lower than the summer peak (as may be the case in the winter, spring and fall days), the loading on the Sargent-Poncha 115kV line would be higher than the summer peak conditions.  For purposes of this discussion, let’s assume the load is 44 MW, or 32% of the 139 MW peak, leaving 214 MW to be exported out of the valley.  With an outage of the Poncha-San Luis 230kV line, the San Luis-Sargent 115kV line would carry 214 MW (rated 159 MW) and the Poncha-Sargent 115kV line would carry 206 MW (rated 128 MW).  So the total length of the Poncha-San Luis 115kV line is overloaded.  Now, the voltage collapse flag for the electric system connected to the Poncha 115kV bus is raised higher.  So obviously the generation would have to be reduced at least 78 MW so as to not overload the Poncha-Sargent 115kV line.

In Mr. Dauphinais’ study approach, because of this heavily loaded 66 mile 	Poncha-San Luis 115kV line, a stability study would need to be done to determine if this 	scenario is transiently stable.  Due to peak load voltage concerns and transient stability 	concerns which can be made worse at the times when the load in the San Luis Valley will 	be less 	than 125 MW, the 250 MW scenario is suspect for feasibility.

In addition, Public Service Company of Colorado (Public Service) does not have firm transmission rights on Western Area Power Administration’s (Western) Poncha-Midway 230kV line nor the Poncha-Curecanti 230kV line.  With 250 MW of generation in the San Luis Valley, Public Service and Western would need to do studies to determine the required amount of firm transmission service, if available.  Since this power would likely mainly be Public Service’s responsibility, PSCo and Western would have to work out a contractual relationship for Public Service’s use of Western’s system.

- STABILITY IS AN ISSUE YOU KEEP RAISING WITH REGARD TO MR. DAUPHANAIS’ PROPOSALS.  YOU DISCUSS ON PAGE 5, LINES 1 TO 7, OF YOUR ANSWER TESTIMONY THE USE OF THE SWING EQUATION TO RAISE STABILITY CONCERNS.  IS IT POSSIBLE TO USE THE SWING EQUATION TO LOOK AT YOUR STABILITY CONCERNS WITH MR. DAUPHANAIS’ PROPOSALS?

- Yes, but let me discuss the swing equation further in this testimony.  Mr. Dauphinais and I discussed in a telephone conversation on November 23, 2009 the swing equation as presented in my Answer Testimony.  Mr. Dauphinais clarified that the swing equation requires a 90 degree number for the δ portion of the swing equation as used in technical reference books.  That makes Sine 90 equal to 1.0 and therefore Pmax equals 1301 MW for the benchmark study I discussed in my Answer Testimony.

- DO YOU AGREE WITH MR. DAUPHINAIS’ CLARIFICATION?

- Yes.  However, the Pmax equals 1301 MW number does not make sense to me.  It is way too high.  In my experience doing stability studies with conditions similar to the instant scenario, the number should be closer to 400 MW.  As stated in my Answer Testimony, stability studies should have been run to test the bench mark study.  Stability studies definitely have to be run to test the proposed San Luis-Calumet-Comanche project.

Q.	DOES MR. DAUPHINAIS’ CLARIFICATION REGARDING THE SWING EQUATION 	PRECLUDE YOU FROM USING IT TO CONSIDER STABILITY?

A.	No, I believe it is still a very useful tool.  Let me elaborate.  For the San Luis Valley area, there are long distances between load serving substations on the 115kV and 230kV system from the San Luis Substation.  The longer the distances, the larger the reactance (X in the denominator of the swing equation) becomes while the angle δ increases getting closer to 90 degrees.

Q.	WHAT ABOUT THE 525 MW GENERATION SCENARIO WITH A PONCHA 	230-115KV TRANSFORMER AND A REMEDIAL ACTION SCHEME?

A.	Using the same reasoning as in the 250 MW case discussed above, the 525 MW 	generation scenario plus 8 MW existing with a 139 MW load would leave 394 MW to be 	exported out of the area over the 115kV and 230kV lines to the Poncha Substation.   The 	394 MW would have a significant impact on Western’s 230kV lines out of the Poncha 	Substation.  The 394 MW would definitely require a careful look and study on the 	impact it would have on Western’s 230kV and 115kV electric system as well as others 	that would now be impacted due to the addition of the Poncha 230-115kV transformer.  	In addition, Western would have to investigate the feasibility and the contractual 	implications on its system out of the Poncha Substation followed by contract negotiations 	between Western and Public Service.  It is unclear how much time these studies and 	contract issues would take to do, however it typically takes years rather than a few 	months to complete.

For an example of transmission costs associated with needing to export 394 MW 	out of the San Luis Valley, let’s assume that 100 MW could be handled by Public 	Service’s 115kV system leaving 294 MW of wheeling from Western, assuming Western 	has transmission capacity for this amount.  Western’s present firm transmission charge is 	$1.48/kW-month or $17.76/kW-year (reference Exhibit IGD-11).  For 294 MW, 	the 	firm transmission cost would be approximately $5.2 million a year ($17.76/kW-	year*294 MW*1000kW/MW).  This cost would need to be considered with Mr. 	Dauphinais’ proposal.  An equivalent Public Service capital investment for transmission 	would be about $34.7 million.

Q.	WHAT COMMENTS DO YOU HAVE REGARDING THE REMEDIAL ACTION 	SCHEME PROPOSED BY MR. DAUPHINAIS?

A.	A remedial action schemes (RAS) is used in the utility industry to take care of special system conditions and the system disturbances that may occur during those special system conditions.  The use of a RAS typically means that there is not enough transmission system to take care of the specified system disturbance.  A RAS has an inherent risk that it may fail to operate as planned.  Many of the blackouts experienced in the Western  Electric Coordinating Council were as a result of failed RAS’s.  Mr. Dauphinais proposes to trip generation with an outage of the San Luis-Poncha 230kV line, a single transmission facility, typically referred to by the utility industry as an N-1 contingency.  For argument sake, let’s assume that out of the 533 MW of solar generation, 135 MW are connected to the 115kV system and the remaining 398 MW are connected to the 230kV system.  With an outage of the San Luis-Poncha 230kV line during a 139 MW peak and  maximum generation, if the RAS failed, about 398 MW of power would need to flow on the 300 MVA 230-115kV San Luis Substation, loading the transformers to 133%.  About 409 MW would also need to flow over the San Luis-Sargent 115kV line, rated at 159 MVA, or a 264% loading.  The Sargent-Poncha 115kV section is rated at 128 MVA and it would need to carry 394 MW, or a 308% loading.  At this loading, the 115kV line would open up (or be severely damaged) isolating the generation, which would then trip off-line on overspeed.  The San Luis Valley would then experience a blackout.  Obviously, the situation would be worse during lower load periods and full generation.

I am not in favor of a RAS in general, especially with a RAS associated with new generation and the concept of skimping on necessary transmission given that the cost of new generation far exceeds the cost of transmission.  Transmission lines stretching 100 to 150 miles are absolutely necessary to deliver the power to the load center under N-1 criteria, which costs roughly 10% of the generation costs of coal fired generation.  Certainly, a RAS that results in load shedding should be scrutinized by the Commission to the extent that load serving reliability is compromised.  For this reason, I do not recommend the use of a RAS to accommodate 525 MW of new generation in the San Luis Valley.

- COMMENTS REGARDING THE ADDITION OF

ANOTHER PONCHA-SAN LUIS 230KV LINE AND THE

475-575 MW OF NEW GENERATION THIS NEW LINE

CAN SUPPORT IN THE SAN LUIS VALLEY

Q.	WHAT ARE YOUR COMMENTS REGARDING THE ADDITION OF

ANOTHER PONCHA-SAN LUIS 230KV LINE AND THE 475-575 MW OF 	NEW 	GENERATION THIS NEW LINE CAN SUPPORT IN THE SAN LUIS VALLEY?

- Another or a second Poncha-San Luis 230kV line in the San Luis Valley would certainly take care of the load serving reliability issue with the outages of the existing Poncha-San Luis 230kV line.  If the new 230kV line replaced the San Luis-Sargent-Poncha 115kV line, a 230-69kV transformer would be required at the Sargent Substation to serve the load at that location.  A new 230-115kV transformer would then be needed at the Poncha Substation to maintain the 115kV interconnection and 115kV point of delivery to the 115kV lines at the Poncha Substation.

My comments here are similar to the previous discussion where these 475-575 MW of generation are mentioned.  The issues that arise and must be resolved have to do with the 115kV and 230kV transmission systems from the Poncha Substation and beyond where the Utilities will be interfacing with Western’s transmission system, among others.  Transmission studies, including stability, need to be done to identify problems and solutions to the problems identified.  As mentioned previously, transmission service contractual issues with Western would also need to be identified and resolved.

V.  COMMENTS REGARDING HOW MR. DAUPHINAIS’ PROPOSAL

IS A SHORT TERM SOLUTION TO THE POTENTIAL OF SOLAR GENERATION IN THE SAN LUIS  VALLEY

Q.	IN REFERENCE TO THE SOLAR GENERATION POTENTIAL IN THE SAN LUIS VALLEY, WHAT ARE YOUR COMMENTS REGARDING MR. DAUPHINAIS’ PROPOSAL THAT YOU DISCUSS ABOVE IN CONNECTION WITH SAN LUIS VALLEY GENERATION IN THE 475-575 MW RANGE?

A.	Mr. Dauphinais’ proposal of a second Poncha-San Luis 230kV line, coupled with Public Service’s proposed addition of a Poncha 230-115kV transformer, certainly has merit to solve the load serving reliability issue in the San Luis Valley.  While these transmission facility additions will take care of load serving reliability issues, the immediate transmission issues associated with new generation in the San Luis Valley shift over to the Poncha Substation and the 230kV and 115kV electric systems connected to it.  As discussed previously, studies in conjunction with Western and other affected utilities in the area need to be done to look at what transmission facilities are needed at the Poncha Substation and beyond.  These studies will determine the transmission facilities needed to accommodate different generation levels in the San Luis Valley area.  These studies can then be used to stage the transmission system with each generation addition in the San Luis Valley area.

However, as I discussed in my Answer Testimony, the solar generation potential in the San Luis Valley is 240,000 MW.  Limiting generation in the San Luis Valley to 400-500 MW therefore seems shortsighted.  Public Service considered a 600 MW level in its studies.  I looked at an 800 MW level at the San Luis Substation combined with 1000 MW at the Calumet Substation to evaluate transmission loss savings with a San Luis-Calumet double circuit 345kV when compared to a double circuit 230kV line.  In some of its earlier studies, the Colorado Long-Range Transmission Planning Group looked at 1000 MW in the San Luis Valley.  Although it is difficult to imagine developing its full 240,000 MW potential, a 2000 MW level, which is less than 1% of the total, seems like a realistic number.  Based on the concepts presented in my Long Term Transmission Study for Colorado (reference Exhibit IGD-12) the 2000 MW level looks reasonable for transmission planning purposes.  Based on that study (reference Exhibit IGD-12, page 36), in my Answer Testimony I presented a 2041 heavy summer case with 1700 MW of generation in the San Luis Substation and 776 MW at Walsenburg Substation (reference Exhibits IGD-7 and 8 attached to my Answer Testimony).  This case represented a need for a San Luis-Walsenburg-Comanche double circuit 345kV line based on the line loadings beyond what a double circuit 230kV line could accommodate.  Obviously, a 2000 MW level of generation would need the double circuit 345kV line.  Note that Exhibit IGD-8 in my Answer Testimony shows a Poncha-Sargent-San Luis 230kV line and a Poncha 230-115kV transformer that complements the San Luis-Walsenburg-Comanche double circuit 345kV line.

Q.	ASSUMING A GENERATION LEVEL IN THE 1700-2000 MW RANGE, COULDN’T A TRANSMISSION SYSTEM GOING NORTH VIA THE EXISTING SAN LUIS-PONCHA TRANSMISSION CORRIDOR BE PLANNED INSTEAD OF A NEW SAN LUIS-CALUMET TRANSMISSION CORRIDOR?

A.	The simple answer is yes, it is possible.  However, there are two major issues that need to be resolved.  The first issue is finding a suitable transmission corridor for the required transmission system.  The second issue is the reliability of the generation transmission system with it being in a common corridor.  I will discuss these two issues separately.

Q.	PLEASE DISCUSS THE TRANSMISSION CORRIDOR ISSUE.

A.	I believe that a 1700-2000 MW power plant complex in the San Luis Valley area will still require the two San Luis-Poncha 230kV circuits as previously discussed and a double circuit 345kV line.  Conceptually, for purposes of this discussion, the first section of this double circuit 345kV line would likely follow the San Luis Substation to the Poncha Substation route, a distance of about 60 miles.  From the Poncha Substation, this double circuit 345kV would probably then proceed to the Midway Substation to interconnect with the Midway-Daniels Park/Waterton 345kV system, a distance of 124 miles.  From the Poncha Substation two new 230kV circuits would be needed.  One circuit could be done by upgrading the Poncha-Malta single circuit 115kV line to a double circuit 230kV line with one side operated at 115kV and the other side at 230kV, a distance of 52 miles.  This construction would maintain the Poncha-Malta 115kV line and create a new Poncha-Malta 230kV line.  The second circuit could be done by upgrading the Poncha-Canon City-West Station-Comanche 115kV line to a double circuit 230kV line to maintain the 115kV circuit and to create a new Poncha-Comanche 230kV circuit, a distance of 130 miles.  A 345-230kV substation would be created at Poncha with 345-230kV transformers added as required at the Poncha Substation and Midway Substation.  With the Poncha-Comanche 230kV circuit, 230-115kV transformers would be added as required.  An equivalent system to the San Luis-Calumet-Comanche proposed transmission project would include the San Luis-Poncha-Midway double circuit 345kV line and the Poncha-Comanche 230kV line.  A rough estimate of the above 345kV line is about $249 million and for the 230kV line it is about $150 million; two 345-230kv transformers would cost about $26 million.  The total cost is about $400 million.  Of course, this new transmission would have to be modeled and tested to make sure that it would work.

In describing this new system, please note I have portrayed the system as following existing transmission corridors.  However, this does not mean they are easily expandable to build new transmission lines.  We only know that they are there.  The local permitting jurisdictions would still need to be approached for permits for rights-of-way (ROW) acquisitions.  Western would probably enter into the picture as a joint participant in the project with all of its federal mandates/requirements for upgrading existing lines and/or building new lines.  In short, the ROW permitting process would be starting over.

Lastly, I acknowledge the construction of the above described facilities will be

much more expensive than the proposed San Luis-Calumet-Comanche transmission project.

Q.	PLEASE DESCRIBE THE GENERATION/ TRANSMISSION RELIABILITY ISSUES.

A.	There are two reliability issues with the system as I described in my response to the previous question.  The first issue is that the two 230kV circuits and the two 345kV circuits carrying the 1700-2000MW are all in the same San Luis-Poncha transmission corridor.  The obvious problem is the simultaneous loss of all the circuits and the subsequent loss of all the generation.  The second issue is a common termination point for all the circuits at the Poncha Substation.  Although the substation would be constructed to properly terminate all the lines in a reliable configuration, the Poncha Substation would present a common point of failure for a severe disturbance, such as a fault at the substation and a breaker failure.  The whole 1700-2000 MW would be at risk.

The San Luis-Calumet-Comanche transmission project provides two transmission outlets and terminations from the San Luis Substation—one to the proposed Calumet Substation and one to the existing Poncha Substation.  This system by design would be a more reliable system than having all the circuits in one corridor with a common termination at the Poncha Substation.

VI.   CONCLUSIONS

Q.	WHAT ARE YOUR CONCLUSIONS FROM YOUR DISCUSSION?

A.	After reviewing Mr. Dauphinais’ testimony, my conclusions are as follows:

1.	Mr. Dauphinais states that 150 MW of new solar generation in the San Luis Valley will take care of the load serving reliability concern.  I disagree.  Mr. Dauphinais’ opinion would typically be true for a more conventional generation.  However, in this case, the new generation is solar with storage that will be on at full capacity when the sun shines during day time hours.  At night the generation will be off line.  During the night, the load typically reduces significantly well below the daily peak, particularly during the fall, winter, and spring months.  During these off peak periods when the generation is off and when the load in the San Luis Valley exceeds 65 MW, the system will be at risk of a voltage collapse with an outage of the Poncha-San Luis 230kV line.  Only when the sun shines during the day will the generation take care of the reliability concern.

2.	Mr. Dauphinais states that significant generation up to 525 MW could be added in the San Luis Valley with Public Service’s proposed Poncha 230-115kV transformer and a remedial action scheme (RAS) where generation is tripped with the loss of the Poncha-San Luis 230kV line.  There are two problems with this idea.  The first is RAS sometimes fail to operate when they should.  Although the loss of a transmission line with a RAS failure may be rare, it is not a good practice to start when the consequences of RAS failure are high.  Should a RAS failure occur in this system design, there is great potential for facility damage and the subsequent loss of load.  The Commission should rule against transmission related RAS that result in loss of load.  The second problem is that the 230kV transmission system from the Poncha Substation cannot accommodate the proposed additional Public Service generation.  Public Service does not have 230kV transmission rights beyond the Poncha Substation.  And, it is not known as this time whether Western has firm transmission capacity that will be available to Public Service.

3.	Mr. Dauphinais’ proposal of a Poncha-Sargent-San Luis 230kV line coupled with Public Service’s proposed Poncha 230-115kV transformer is a good long term  solution to the load serving reliability issue in the San Luis Valley.  However, Mr. Dauphinais’ claim that these project additions can accommodate 475-575 MW with other minor transmission additions is premature.  As previously discussed, the 115kV and 230kV system from the Poncha Substation and beyond requires further analysis, including the capabilities of Western’s system.

4.	Mr. Dauphinais’ proposal of limiting the San Luis generation to a 475-575 MW range while expanding the generation in the Walsenburg/Calumet area beyond that range is short sighted when considering the San Luis Valley solar generation potential of 240,000 MW.  At this level of potential, a 2000 MW solar generation development in the San Luis Valley, or less than 1%, appears reasonable.  A 2000 MW generation level would require a transmission system equivalent to the San Luis-Calumet-Comanche transmission project with the San Luis-Calumet line being a 345kV line in addition to a new Poncha-San Luis 230kV line.  A 2000 MW generation scenario would also require studying what other transmission lines may be required at the Poncha Substation and beyond.

5.	With the great solar generation potential in the San Luis Valley, it makes sense to apply a long term planning concept of a potential 2000 MW generation complex in the San Luis Valley area and plan a transmission system consistent with that generation level, which is also consistent with the legislative intent of Senate Bill 07-100.  For reliability and economic reasons, a new transmission corridor that includes a San Luis-Calumet double circuit 345kV line makes for long term planning sense.

VII.     SUMMARY AND RECOMMENDATIONS

Q.	PLEASE SUMMARIZE STAFF’S RECOMMENDATIONS.

A.	Staff’s most significant recommendations are as follows:

1.	Staff agrees with Mr. Dauphinais that a generation level of 150 MW that closely matches the load could be installed in the San Luis Valley without major transmission additions.  However, it should be understood that solar generation may not be on when the sun does not shine and the load may be above 65 MW during those times requiring to import the power from the Poncha Substation into the San Luis Valley area.  This scenario maintains the voltage collapse risk with the outage of the San Luis-Poncha 230kV line.

2.  	Staff agrees with Mr. Dauphinais that generation tripping remedial action schemes (RAS) may be used to maintain higher generation levels then the transmission system may typically allow with an N-1.  However, the generation levels considered by Mr. Dauphinais in the San Luis Valley have an inherit high risk of potential transmission facility damage and loss of load with a RAS failure together with an outage of the Poncha-San Luis 230kV line.  For this reason, the Commission should reject this recommendation.

3.	Staff disagrees with Mr. Dauphinais that generation levels in the 525 MW range will require minor transmission fixes at Poncha Substation and beyond.  Public Service does not have 230kV transmission service rights at the Poncha Substation on Western’s system.  Western may not have firm transmission available for Public Service’s use.  The Commission should not accept Mr. Dauphinais’ testimony since, at this time, Western and Public Service have not negotiated a contractual relationship whereby Public Service is assured firm transmission capacity from Western’s system.

4.	Staff agrees with Mr. Dauphinais that a second Poncha-San Luis 230kV line coupled with a Poncha 230-115kV transformer takes care of the load serving reliability issue in the San Luis Valley.  However, Staff disagrees that these two transmission facility additions can accommodate generation in the valley in the 475-575 MW range with minor transmission facility fixes at the Poncha Substation and beyond.  Public Service does not have transmission service rights on Western’s 230kV system at the Poncha Substation and it is not known whether Western has firm transmission capacity to offer Public Service.  A joint study involving the affected utilities with transmission facilities at the Poncha Substation needs to be done to determine the problems and solutions, in addition to negotiating and settling transmission contract issues between Public Service and Western.  For these reasons, the Commission should question the generation levels as proposed by Mr. Dauphinais.

5.	Staff disagrees with Mr. Dauphinais to limit the generation level in the San Luis Valley to about 525 MW consistent with what a second Poncha-San Luis 230kV line coupled with a Poncha 230-115kV transformer would allow.  This generation level is shortsighted.  The potential solar generation level in the San Luis Valley is 240,000 MW and therefore a 2000 MW level appears reasonable as it is  consistent with long term planning concepts and the legislative intent of Senate Bill 07-100. Staff recommends that the Commission maintain a long term planning concept consistent with a 2000 MW generation approach and reject Mr. Dauphinais’ recommendation.

6.	Staff recommends the Commission adopt the concept of a new San Luis-Calumet-Comanche double circuit transmission line to allow for a potential 2000 MW generation complex in the San Luis Valley and to improve the load serving reliability in the San Luis Valley.  As I stated in my Answer Testimony, with generation in the San Luis Valley greater than 800 MW, the losses savings start to be significant enough to justify the construction of the San Luis-Calumet transmission line for 345kV.  As 2000 MW of generation will require the San Luis-Calumet line to be a double circuit 345kV line, it makes sound long term planning and economic sense to initially construct the San Luis-Calumet line for 345kVeven if it is initially operated at 230kV until 345kV operation is required.

Q.	DOES THAT CONCLUDE YOUR TESTIMONY AT THIS TIME?

A.	Yes, it does.

BEFORE THE PUBLIC UTILITIES COMMISSION

STATE OF COLORADO

DOCKET NO. 09A-324E

AND

DOCKET NO. 09A-325E

IN THE MATTER OF THE application of TRI-STATE GENERATION AND TRANSMISSION ASSOCIATION, INC., AND PUBLIC SERVICE COMPANY OF COLORADO, (a) FOR A CERTIFICATE OF PUBLIC CONVENIENCE AND NECESSITY FOR THE SAN LUIS-CALUMET-COMANCHE TRANSMISSION LINE PROJECT, (b) FOR SPECIFIC FINDINGS WITH RESPECT TO EMF AND NOISE, AND (c) FOR APPROVAL OF OWNERSHIP INTEREST TRANSFER AS NEEDED WHEN PROJECT IS COMPLETED.

I, Inez G. Dominguez, being duly sworn, state that the attached testimony was prepared by me or under my supervision, control, and direction; that the testimony is true and correct to the best of my information, knowledge and belief; and that I would give the same testimony orally if asked under oath.

__________________________________

Inez G. Dominguez

Subscribed and sworn to before me in the County of                     , State of Colorado, this       day of _____________________ 2009.

NOTARY PUBLIC

My Commission expires:

___________________________

Utility’s typically use a Fixed Charge Rate (FCR) to levelize on an annual basis the revenue requirements of a capital project.  The levelized annual cost is obtained by multiplying the total capital dollars by the FCR, which generally is 15% for transmission lines.  To get an equivalent capital dollars cost by having an annual cost, the annual cost is divided by the FCR.  In this example, the $5.2 million is divided by 0.15 to get $34.7 million.

Costs were provided by Tri-State for a double circuit 345kV line and a double circuit 230kV line.  The average cost for the 345kV line was $1,354,714 per mile and for the 230kV line $961,842 per mile.  The $26 million for the 345-230kv transformers was my estimate based on the average cost per transformer for the Comanche 3 transmission system.